## Slide 1
1
2. Incidence of Lightning to Areas and Structures

## Slide 2
Course Sections | Number of Lectures | HW Due (Can-vas) | Test (Honor-lock) | Section in Course Packet | Chapter/ Sections in Text (FOL)
Introduction | 1 |  |  |  | 
1. Types of lightning discharges and lightning terminology | 4 | HW1 01/25 | T1 01/27 | 1 | 1, App. 1, 4
2. Incidence of lightning to areas and structures | 4 | HW2 02/05 | T2 02/08 | 2 | 2, Sect. 9.3
3. Electrical structure of thunderstorm clouds | 6 | HW3 02/22 | T3 02/24 | 3 | 3, App. 2
4a. Properties of the negative lightning discharge to ground - I | 5 | HW4 03/08 | T4 03/10 | 4a | 4.1-4.3, 4.6, 4.10
4b. Properties of the negative lightning discharge to ground – II | 4 | HW5 03/19 | T5 03/22 | 4b | 4.4-4.5, 4.7-4.10, 9.3

## Slide 3
A global map of total lightning flash density (per square kilometer per year) based on data from two satellite detectors, Optical Transient Detector (OTD, 5 years) and Lightning Imaging Sensor (LIS, 3 years).
Grey areas: 0.01-0.1 km-2yr-1; white areas: <0.01 km-2yr-1.
Total (Ng + Nc) Lightning Flash Density Map
(Ng/(Ng + Nc) = 1/4 is needed to obtain Ng); Ng = 0.25(Ng+ Nc)
3
Notes: 3

## Slide 4: Ground Lightning Flash Density (Ng) – 15 years (1997-2011) of observations
4
Notes: 4

## Slide 5
U.S. National Lightning Detection Network
47 IMPACT Sensors (red triangles); 59 LPATS/III Sensors (blue circles)
5
Notes: 5

## Slide 6
Data flow in the U.S. National Lightning Detection Network (NLDN). Actual system employs three satellite downlink locations represented by item 3.
The NLDN has been providing real-time, continental-scale lightning data since 1989. The most recent network-wide NLDN upgrade was conducted in 2002-2004.
U.S. National Lightning Detection Network (NLDN)
6

## Slide 7
7
Ground Lightning Flash Density (Ng) – South Africa
CIGRE 10 kHz lightning flash counters, 1975-1986 (11 years)

## Slide 8: A map of mean annual number of thunderstorm days (TD) for the United States based on data from 450 air weather stations shown as dots. Most stations had 30-year records and all at least 10-year records. Adapted from MacGorman et al. (1984).

## Slide 9
9
Ng = 0.04 TD1.25

## Slide 10
Sequence of events in classical (grounded-wire) negative rocket-triggered lightning (rocket is needed only to extend the wire to a height of a few hundred meters). Adapted from Rakov (1999).
Leader/RS Sequence
Initial Stage
10
Rocket-and-wire lightning triggering technique
E-field

## Slide 11
Types of lightning discharges from cumulonimbus (thunderclouds)
Cloud-to-ground (25%)
Cloud-to-air
Intracloud
Cloud-to-
cloud
Cloud discharges (75%)
11
Types of Lightning Discharges and Lightning Terminology
11
Notes: 11

## Slide 12
12
Lightning Incidence to Structures
N = (Nd + Nu) yr-1
Empirical formulas:
N = 24 x 10-6 Hs2.05 Ng, where Hs is in meters and Ng is in km-2 yr-1 ( for Hs> 20 m).
Percentage of upward flashes, % :
Pu = 52.8 ln Hs – 230, where Hs is in meters.
Ng = 0.04 TD1.25

## Slide 13
N is about 23 yr-1, Pu = 96% (percentage of upward flashes)
Empire State Building (Hs = 400 m), New York City, USA, TD = 31 yr-1

## Slide 14
14
Number of Lightning Strikes to a Structure - Nd
When the incidence of only downward lightning strikes is concerned, it is common to ascribe the so-called equivalent attractive area to a ground-based object. It can be defined as ground-surface area that would receive the same number of strikes as the structure, provided that Ng=const:
Nd = A x Ng
For a free-standing structure, such as a mast or chimney, this area circular and is given by
where Ra is the equivalent attractive radius.

## Slide 15
For stretched structures (such as a power line) the equivalent attractive area is rectangular and is sometimes termed the "shadow zone" or "attractive swath" and expressed as
where, for power lines, L is the line length, b is the line effective width, and Ra is the equivalent attractive distance, thought to be equal to the equivalent attractive radius for a free-standing structure of the same height. b is usually taken as the distance between overhead ground wires ( b = 0 for a single ground wire).

## Slide 16
16
Number of Lightning Strikes to a Structure - Nd
Attractive radius Ra is usually assumed to be a function of structure height h ( for h < 100 m):
where a and b can be estimated from
using actual data on Ng and lightning incidence Nd to structures of different height h as
where Ng = 0.04 TD1.25
Nd = (πRa2) x Ng

## Slide 17
According to the IEEE Std 1243,
and the transmission-line flash collection rate, Ns (in strikes/100 km/yr) is
where h and b are in meters and Ng in flashes/km2/yr (L = 100 km).
(Ra = 2h for rough estimates)

## Slide 18: Power transmission lines, each having three phase conductors (labeled PC), suspended on metallic towers using insulators, and two overhead ground wires (labeled OGW) , installed above phase conductors for lightning protection. Courtesy of Mannvit Engineering.

## Slide 19: (a) Schematic representation of power transmission line having three phase conductors (labeled PC) and two overhead ground wires (labeled OGW), the latter being separated by distance b. Also shown is the attractive distance Ra and the width W of equivalent attractive area A of the line. (b) Illustration of the OGW mid-span sag d, which is used for estimating the effective height h of the line. Artwork by Potao Sun.

## Slide 21
Number of years of observation, T | Number of times struck by lightning, n |  |  |  | 
 | 0 (0! = 1) | 1 | 2 | 3 | >3
10 | 191 | 9 | 0 | 0 | 0
20 | 182 | 17 | 1 | 0 | 0
30 | 173 | 25 | 2 | 0 | 0
40 | 165 | 32 | 3 | 0 | 0
50 | 157 | 38 | 5 | 0 | 0
60 | 150 | 43 | 6 | 1 | 0
70 | 143 | 48 | 8 | 1 | 0
80 | 136 | 53 | 10 | 1 | 0
90 | 130 | 56 | 12 | 2 | 0
100 | 124 | 60 | 14 | 2 | 0
Number, N = 200 p(n), of houses out of a total of 200 (percentage if divided by 2) expected to be struck by lightning n times over T years (Ng = 4 km-2 yr-1; A = 1200 m2)
Poisson probability distribution: p(n) = (Zn/n!)exp(-Z), where Z = ANgT
If Ng = 12 km-2 yr-1 ,
T = 60 yrs, N(0) = 84 and N(≥3) = 11
p(n ≥ 0) = 1
p(n > 1) = 1 – p(0) – p(1)

## Slide 22
22
Electrogeometrical model (EGM)

## Slide 23
Illustration of the definitions of striking distance (rs)
It is assumed that the downward leader tip is at striking distance (rs) from the prospective strike point when the upward connecting leader (UCL) is initiated at that point.
The higher the downward leader potential (charge and prospective return-stroke current), the larger the striking distance). The striking distance is expressed as a function of peak current, rs = f(I).
UCL is initiated when the E-field across the gap exceeds about 500 kV/m

## Slide 24
24
Scatter plot of impulse charge, Q, versus return-stroke peak current, I. Note that both vertical and horizontal scales are logarithmic. The best fit to data, I = 10.6 Q0.7, where Q is in coulombs and I is in kiloamperes, was used in deriving rs = 10 I0.65 Adapted from Berger (1972).
Electrogeometrical Model (EGM) – Striking Distance rs
Finding rs = f(I)
Assume critical average electric field between the leader tip and the strike object at the time of initiation of upward connecting leader from the object (200-600 kV/m)
Use an empirical
relation between Q and I
to find rs = f(I)
Find rs = f(Q)
Assume leader geometry, total leader charge Q, and distribution of this charge along the channel.
Q
10-1
100
101
102
100
101
102
I
I peak/ Q impulse
neg. first strokes
n=89
I = 10.6 Q0.7
For Q = 5 C
I = 33 kA
Notes: 24

## Slide 25
25
Electrogeometrical Model (EGM)
rs = 10 I0.65, m where I is in kA
4
3
1
2
Striking distance, rs, versus return-stroke peak current, I [curve 1, Golde (1945); curve 2, Wagner (1963); curve 3, Love (1973); curve 4, Ruhling (1972); x, theory of Davis (1962); , estimates from two-dimensional photographs by Eriksson (1978); , estimates from three-dimensional photography by Eriksson (1978). Adapted from Golde (1977) and Eriksson (1978).
I, kA | rs, m
10 | 45
30 | 91
170 | 282
{
Notes: 25

## Slide 26
26
Illustration of capture surfaces of two towers and earth’s surface in the electrogeometrical model (EGM). rs is the striking distance defined as the distance from the tip of the descending leader to the object to be struck at the instant when an upward connecting leader is initiated from this object. Vertical arrows represent descending leaders, assumed to be uniformly distributed (Ng=const) above the capture surfaces. Adapted from Bazelyan and Raizer (2000).
Electrogeometrical Model (EGM)
rs
rs
rs
Capture surfaces
Ng=const
S1
S2
Notes: 26

## Slide 27
27
Electrogeometrical Model (EGM)
Illustration of the rolling-sphere method (RSM). The shaded area is that area into which, it is postulated, lightning cannot enter. Adapted from Szczerbinski (2000).
rs
rs
rs
rs = 45 m (150 ft)
(NFPA 780, 2004),
corresponds to I = 10 kA
(95% of currents exceed this value)
Rolling-Sphere
Method (RSM)

## Slide 28
28
RSM, 10 kA, rS = 45 m
28

## Slide 29
29
RSM, 170 kA, rS = 282 m
29

## Slide 30
Final design
30
Mata and Rakov (2008)

## Slide 31
31
Lightning Incidence – Florida (1989-1995, 7 years)

## Slide 32: A world map of mean annual number of thunderstorms days. Adapted from WMO Publication 21 (1956).

## Slide 33: Recommended Empirical Formulas
Ground Flash density, km-2 yr-2 :
Ng = 0.04 TD1.25 (Ng =0.1 TD for rough estimates)
Ng = 0.054 TH1.1 (Ng =0.05 TH for rough estimates)
Lightning incidence to towers ( for Hs> 20 m), yr-1 :
N = 24 x 10-6 Hs2.05 Ng, where Hs is in meters and Ng is in km-2 yr-1
Equivalent attractive radius (distance), m:
Ra =14 Hs 0.6 , where Hs≤ 100 m (Ra = 2Hs for rough estimates)
Percentage of upward flashes, % :
Pu = 52.8 ln Hs – 230, where Hs is in meters

## Slide 34
34
Interaction of Lightning with Power Lines (shielding failure, back-flashover, induced effects)

## Slide 35
35
Lightning Interaction with Power Lines
Phase Conductor
Overhead Ground Wire
Insulator String
Double-circuit vertical conductor configuration
Single-circuit horizontal conductor configuration
Overhead Ground Wires
Insulator String
Phase Conductor
Strike to ground wire
Strike to phase conductor
Strike to ground
(Uman, 1986)

## Slide 36
36
Induced Overvoltages
Relationship between induced voltage amplitude and flash distance.
Induced voltages were measured on the10-km wood-pole test line, approximately 8 m high, about 400-500 kV impulse insulation level.
(Eriksson and Meal, 1984)
HV
EHV

## Slide 37
37
Lightning Incidence to Electric Power Lines
(Gorin et al., 1978)
Average annual number of direct lightning strikes to power lines of different height (per 100 km, normalized to 26 thunderstorm days)
1 – Stekolnikov and Lamdon (1938)
2 – Lewis and Foust (1937)
3 – Waldorf (1941)
4 – Hansson and Waldorf (1944)
5 – Schlomann et al. (1958)

## Slide 38
38
SF: If a phase conductor is struck, a comparatively small current acting through the conductor surge impedance will build up a voltage that will flash over the line insulation. For example, 7.5 kA (more than 95% probability of occurrence) acting through 400 ohm surge impedance will build up 3 MV on the conductor.
BF: If the line is equipped with overhead ground wires, and a ground wire is struck, then the impedance through which the current acts is very much reduced, and a corresponding higher current is required to cause flashover. If the impedance is reduced to say 25 ohms, then approximately 120 kA (less than 5% probability of occurrence) would be required to produce the same 3 MV.
(Lewis, 1965)
Back-flashover (BF) vs. shielding failure (SF)
Simplified equivalent circuit
Conclusion:
Need a ground wire to intercept lightning
Notes: 38
38

## Slide 39
39
Lightning Performance of Power Lines

## Slide 40
Poisson’s probability
distribution (gives the
probability of n strikes
in T years)

## Slide 41
U.S. National Lightning Detection Network (NLDN)
A summary of the cloud-to-ground lightning activity reported by the NLDN for the Blizzard of ’93, from 06:02 UT 12 March to 10:02 UT 14 March 1993. The total number of recorded flashes for this time period was 62 887. The dots indicate negative flashes (55 206) and the pluses indicate positive flashes (7681). Different colors correspond to different times, as shown. Courtesy of Global Atmospherics, Inc.
41

## Slide 42
U.S. National Lightning Detection Network (NLDN)
Courtesy of R.E. Orville.
42
Notes: 42

## Slide 43
The percentage of upward flashes from tall structures.
Adapted from Eriksson (1978).
Pu is the percentage of upward flashes.
HS is the structure height in meters.
Reference | Structure height, m | Percentage of upward flashes
Pierce (1972) | 150 200 300 400 | 23 50 80 91
McCann (1944) | 110 180 400 | 8 24 96
Berger (1972) | 350a | 84
Gorin (1972); Gorin et al. (1976) | 540 | 92b
Garbagnati et al. (1974) | 500c | 98
aAn effective height of 350 m has been assigned by Eriksson to Berger's 70 m high mountain-top towers to account for the enhancement of the electric field by the mountain whose top is 640 m above Lake Lugano (914 m above sea level). Pierce (1971) assigned a different effective height of 270-m to the Berger's towers.
b50% of the flashes recorded in this study were classified as 'unidentified'. The relative incidence of upward flashes is based upon analysis of only the identified data.
cGarbagnati et al.'s towers were 40 m high, located on mountain tops, 980 and 993 m above sea level (Berger and Garbagnati, 1984). Eriksson (1978) does not give any explanations of the assumed effective height of 500 m.

## Slide 44
_
– _
_
_
+
+
+ +
+
+
_ _ _ _
_ _ _
_ _ _ _
+
+
+ +
+
+
An object-initiated discharge begins when the electric field intensity over some critical distance from the tip of object exceeds the breakdown value.
An in-cloud or nearby ground discharge creating a rapid electric field change (more common scenario; 10 out of 14 upward flashes in Wang et al. (2008))
Slow charge build-up in the cloud produced by the cloud electrification processes (3 out of 4 such events in Wang et al. (2008) initiated from rotating windmill)